## Slide 1: LHConCRAY acceptance tests (partial) results
Pablo Fernandez
3rd October, 2017

## Slide 2: Figures from Runs 1-6

## Slide 3: Comparing Phoenix to Piz Daint
Figures collected since the 5th of May until the 1st of October, 2017
3-4 weeks of data on each of the 6 runs (with one exception: run 4 was only 9 days)
Agreed metrics:
  Produced walltime (good & bad) per core, per type of job
  Walltime of good vs failed jobs, per type of job
  CPU/Wallclock efficiency for successful jobs, per type of job
  Site Availability
The magic formula to measure the system performance would be the product of the following wall-time ratios:
  % system capacity occupation
  % successful jobs
  % cpu efficiency of successful jobs

## Slide 4: Per-VO efficiency comparison
Chart: CMS - Good VS Bad %
Phoenix | 0.516 | 0.594 | 0.562 | 0.757 | 0.664 | 0.611
Piz Daint | 0.529 | 0.496
Chart: CMS - CPU efficiency %
Phoenix | 0.8 | 0.859 | 0.728 | 0.867 | 0.929 | 0.966
Piz Daint | 0.871 | 0.859
Chart: LHCb - CPU efficiency %
Phoenix | 0.97 | 0.97 | 0.97 | 0.97 | 0.96 | 0.89
Piz Daint | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.98
Chart: LHCb - Good VS Bad %
Phoenix | 0.95 | 0.96 | 0.98 | 0.98 | 0.92 | 0.77
Piz Daint | 0.9 | 0.85 | 0.8 | 0.92 | 0.91 | 0.93
Chart: ATLAS - Good VS Bad %
Phoenix | 0.87443 | 0.87258 | 0.94585 | 0.93465 | 0.71005 | 0.72
Piz Daint | 0.59673 | 0.76102 | 0.6221 | 0.84695 | 0.86335 | 0.78
Chart: ATLAS - CPU efficiency %
Phoenix | 0.93142 | 0.89072 | 0.70042 | 0.86977 | 0.646 | 0.79
Piz Daint | 0.8418 | 0.8092 | 0.80427 | 0.7793 | 0.85844 | 0.83

## Slide 5: Between-VO statistics
Chart: Capacity Utilization %
Phoenix | 0.88762 | 0.88031 | 0.97662 | 0.94013 | 0.80293 | 0.69891
Piz Daint | 0.42346 | 0.63892 | 0.84186 | 0.68213 | 0.8523 | 0.78041
Chart: Phoenix - Fair Share %
ATLAS | 0.364 | 0.53 | 0.46 | 0.3889 | 0.41 | 0.57
CMS | 0.311 | 0.22 | 0.29 | 0.3488 | 0.39 | 0.32
LHCb | 0.325 | 0.25 | 0.25 | 0.2622 | 0.2 | 0.11
Chart: Piz Daint - Fair Share %
ATLAS | 0.178 | 0.68 | 0.6 | 0.3623 | 0.45 | 0.51
CMS | 0 | 0 | 0 | 0.0718 | 0.17 | 0.24
LHCb | 0.822 | 0.32 | 0.4 | 0.5658 | 0.39 | 0.25

## Slide 6: How can we compare both systems today?
Using the magic formula
  System = % system capacity occupation * % successful jobs * % cpu efficiency of successful jobs
  Average all VOs by their 40:40:20 ratio
  HS06 difference (12.81 HS06/core in Piz Daint, 11.19 in Phoenix) of +14% in favor of Piz Daint is counted in the price comparison, not here!
Case 1: looking only at Run 6:
  Phoenix: 70% * 69% * 88% = 42.5%
  Piz Daint: 78% * 70% * 87% = 47.5% (11.4% better)
Case 2: looking at both Runs 5 & 6:
  Phoenix: 75% * 71% * 85% = 45.2%
  Piz Daint: 81% * 72% * 88% = 51.3% (13.5% better)
Case 3: Piz Daint runs 5-6 against Phoenix runs 1-3 (downtimes are different!)
  Phoenix: 91% * 77% * 85% = 59.5% (16% better)
  Piz Daint: 81% * 72% * 88% = 51.3%

## Slide 7: Conclusions
Piz Daint started “slow” but has already catch up 2 months ago
CMS is still “young” on Piz Daint, while ATLAS and LHCb are quite mature
If we look at “today”, Piz Daint is 12% better than Phoenix, but current Phoenix “slowdown” reduces the reliability on such number
Note: numbers here are global averages, to be taken with caution.

## Slide 8: Thank you for your attention.